## Slide 1: Bridging the Gap: Answering Questions Through Research
Catherine Hovell, PhD
October 1, 2012
…one direction a UVa degree can take you …

## Slide 2: Flow of Test Program
Can we __________________________?
What about _______________________?
What happens if ____________________?

## Slide 3: Flow of Test Program
Can we optimize the end-region of Texas U-Beams?
  ease construction
  maintain structural performance

## Slide 4: Flow of Test Program
Literature Review:
  What previous testing has been done?
  What is the current performance of the structure?

## Slide 5: Flow of Test Program
test those specimens
build test specimens

## Slide 6: Flow of Test Program
test those specimens
build test specimens
compare results to predictions
gather results

## Slide 7: Flow of Test Program
compare results to predictions
gather results
test those specimens
build test specimens

## Slide 8: Introduction to the Texas U-Beam
Designed in the 1990s as an "aesthetically pleasing" alternative for use in highly visible interchanges

## Slide 9: Introduction to the Texas U-Beam
96"
5"
4
1
55"
54"

## Slide 10: Flow of Test Program
Can we optimize the end-region of Texas U-Beams?
  ease construction
  maintain structural performance

## Slide 11: Flow of Test Program
Literature Review:
  What previous testing has been done?

## Slide 12: Flow of Test Program
Literature Review:
  What previous testing has been done?
    …on U-Beams
    …under shear load

## Slide 13: Flow of Test Program
Literature Review:
  What previous testing has been done?
    …on U-Beams
    …under shear load
Box-Beam 23 (2%)
T-Beam 139 (12%)
Rectangular 299 (26%)
I-Beam 677 (59%)
[ data from UTPCSDB Filtered Database, N = 1138 ]

## Slide 14: Flow of Test Program
Literature Review:
  What previous testing has been done?
    …on U-Beams
    …under shear load
  What is the current performance of the structure?
- not much
- no tests of U-Beams

## Slide 15: Expectations: Shear Strength
University of Texas Prestressed Concrete Shear Database (2011 Edition) [ UTPCSDB-2011 ]
  99 references from 1954-2010
  shear studies from US, Europe, Japan
Used to create an Evaluation Database answering the question – how accurate is the code equation for shear capacity?

## Slide 16: Expectations: Shear Strength
Concrete Strength [ksi]
calculated using AASHTO LRFD General Procedure (2010)
conservative

## Slide 17: Expectations: Shear Strength
Concrete Strength [ksi]
calculated using AASHTO LRFD General Procedure (2010)
conservative
each dot represents a
single laboratory test –
one beam, loaded to failure

## Slide 18: Beam Fabrication
tie reinforcement

## Slide 19: Beam Fabrication
place concrete: fill bottom slab

## Slide 20: Beam Fabrication
place concrete: place void form

## Slide 21: Beam Fabrication
place concrete: fill webs

## Slide 22: Beam Fabrication
place concrete: clean up

## Slide 23: Beam Fabrication
…wait…

## Slide 24: Beam Fabrication
strip forms

## Slide 25: Beam Fabrication
beam is complete!

## Slide 26: Shear Test Setup
Hydraulic rams
Reaction structure
post-tensioned clamps
bars at 4 in.
bars at 6 in.
TEST REGION

## Slide 27: Shear Test Setup
post-tensioned clamps
bars at 4 in.
bars at 6 in.
FAILURE ZONE
Hydraulic rams
Reaction structure
TEST REGION

## Slide 28: Shear Test Setup

## Slide 29: STEP 1: Establish Current Behavior

## Slide 30: Beams 1 and 2
Beam 1
Beam 2
B1N
B1S
B2N
Failure could not be reached
B2S

## Slide 31: Shear Performance: B1N
= [0.71]
[0.89]
Shear Force
Distance from Beam End
#4 stirrups spaced at:
  4 in. for 6'-3"
  6 in. for 7'-1"
B1N = 659 kip
= 0.71

## Slide 32: Shear Performance: B1N
Concrete Strength [ksi]
calculated using AASHTO LRFD General Procedure (2010)
conservative
B1N

## Slide 33: Shear Performance: B1S & B2N
Shear Force
Distance from Beam End
= [0.82]
[0.66]
= 0.66
B1S

## Slide 34: Shear Performance: B1S & B2N
= [0.82]
[0.66]
Shear Force
Distance from Beam End
= 0.66
B1S
= [0.56]
[0.72]
Shear Force
Distance from Beam End
= 0.56
B2N

## Slide 35: Shear Test Setup
bars at 4 in.
bars at 6 in.
EXPECTED
FAILURE ZONE
TEST REGION
B1S
B2N
ACTUAL
FAILURE ZONE
= 0.71, 0.66, 0.56

## Slide 36: Intermediate Analysis
These beams are not failing in web-shear
  Comparing failure shear with code web-shear capacity is inappropriate
Are we testing the worst-case scenario?
Beam 3
B3N
B3S
Contains 42 0.5-in. strands (instead of 78)

## Slide 37: Shear Performance: B3N & B3S
Shear Force
Distance from Beam End
Shear Force
Distance from Beam End
= [0.96]
[1.07]
= 0.96
= [1.08]
[0.97]
= 0.97
B3N
B3S

## Slide 38: Comparison of Failure Shears
Failure Shear, [kip]
B1N
B1S
B2N
B3N
B3S
659 k
612 k
610 k
655k
663 k
0.66
0.56
0.96
0.97
0.71

## Slide 39: Shear Performance: B3S
B3S

## Slide 40: Horizontal Shear
P
reinforcement

## Slide 41: Horizontal Shear
P

## Slide 42: Horizontal Shear
P

## Slide 43: Flow of Test Program
Can we optimize the end-region of Texas U-Beams?
  ease construction
  maintain structural performance
Can we improve the end-region design of Texas U-Beams to increase horizontal shear capacity and allow web-shear to control behavior?

## Slide 44: STEP 2: Design Beams for Better Behavior

## Slide 45: Test Region B4N
#4 R-bars spaced at 3 in. for 5'-0"
4 in. for 5'-0"
6 in. for 3'-4"
modified cross-section
confinement steel
R-bar

## Slide 46: Test Region B4N
Shear Force
Distance from Beam End
horizontal shear with some web crushing
= [0.86]
[1.12]
[0.93]
= 0.86
#4 R-bars spaced at 3 in. for 5'-0"
4 in. for 5'-0"
6 in. for 3'-4"
B4N

## Slide 47: Test Region B4S
#4 R-bars spaced at 3 in. for 5'-0"
4 in. for 5'-0"
6 in. for 3'-4"
3-#5 L-bars spaced at 3 in. for 5'-0"
4 in. for 2'-8"
modified cross-section
confinement steel
supplementary bottom flange-to-web steel (L-bars)
R-bar

## Slide 48: Test Region B4S
Shear Force
Distance from Beam End
#4 R-bars spaced at 3 in. for 5'-0"
4 in. for 5'-0"
6 in. for 3'-4“
3-#5 L-bars spaced at 3 in. for 5'-0"
4 in. for 2'-8"
= 1.37
[1.37]
[1.05]
[1.14]
test halted before failure
B4S
No L-bars

## Slide 49: Test Region B5N
#5 R-bars spaced at 4 in. for 8'-3"
6 in. for 5'-1"
#6 L-bars spaced at 4 in. for 8'-3"
confinement steel
supplementary bottom flange-to-web steel (L-bars)
R-bar

## Slide 50: Test Region B5N
Shear Force
Distance from Beam End
#5 R-bars spaced at 4 in. for 8'-3"
6 in. for 5'-1"
#6 L-bars spaced at 4 in. for 8'-3"
= 1.11
[1.00]
[1.11]
B5N
flexure-shear
6 in. spacing, no L-bars

## Slide 51: Recommended New Design
#4 R-bars (stirrups)
2-#5 L-bars (supplementary steel)
#4 C-bars (confinement)
standard cross-section

## Slide 52: Recommended New Design
3'-0" to 3'-6"
2'-6" to 3'-0"
2'-0" to 2'-6" for beams with skew > 30°
1'-6" to 2'-0" for beams with skew < 30°
CURRENT STANDARD
RECOMMENDED STANDARD

## Slide 53: Recommended New Design
CUT
End-region bottom flange-to-web interface reinforcement, = 1%
Square end block length: 2'-6" to 3'-0"
Square end block length: 1'-6" to 2'-0"
EXISTING TEXAS U-BEAM STANDARD
RECOMMENDED NEW TEXAS U-BEAM STANDARD
R-bar
R-bar
L-bars
End-region bottom flange-to-web interface reinforcement, = 4%
End block vertical reinforcement (V- and F-bars)

## Slide 54: Test Region B6S
Shear Force
Distance from Beam End
[1.27]
[1.09]
B6S
#4 R-bars spaced at 4 in. for 8'-3"
6 in. for 5'-1"
2-#5 L-bars spaced at 4 in. for 8'-3"
flexure-shear
= 1.27
6 in. spacing, no L-bars

## Slide 55: Test Region B7N
B7N
web crushing
= 1.65
Shear Force
Distance from Beam End
[1.33]
[1.65]
#4 R-bars spaced at 4 in. for 8'-3"
6 in. for 5'-1"
2-#5 L-bars spaced at 4 in. for 8'-3"
6 in. spacing, no L-bars

## Slide 56: Effect of Design Changes
[0.56]
[0.72]
Shear Force
Distance from Beam End
= 0.56
B2N
Horizontal Shear Failure
Shear Force
Distance from Beam End
[1.27]
[1.09]
= 1.27
Flexure-Shear Failure
B6S

## Slide 57: Comparison to the Literature
Concrete Strength [ksi]
calculated using AASHTO LRFD General Procedure (2010)
conservative

## Slide 58: Comparison to the Literature
Concrete Strength [ksi]
calculated using AASHTO LRFD General Procedure (2010)
conservative
B5N
B6S
B7N

## Slide 59: Bridging the Gap [ or, Filling Holes in the Literature ]

## Slide 60: New Data in Literature
Shear Test Program
Box-Beam 23 (2%)
T-Beam 139 (12%)
Rectangular 299 (26%)
I-Beam 677 (59%)
U-Beam 11 (1%)
[ data from UTPCSDB Filtered Database, N = 1138 ]

## Slide 61: New Data in Literature
Shear Test Program
[ data from UTPCSDB Filtered Database, N = 1138 ]
Specimen Depth [in.]
Year of Testing
50%
2%

## Slide 62: New Data in Literature
Shear Test Program
Specimen Depth [in.]
Year of Testing
U-Beams: 62.75 in.
[ data from UTPCSDB Filtered Database, N = 1138 ]
50%
2%

## Slide 63: New Data in Literature
Shear Test Program
Shear Area, [in.2]
Year of Testing
60%
1%
[ data from UTPCSDB Filtered Database, N = 1138 ]

## Slide 64: New Data in Literature
Shear Test Program
Shear Area, [in.2]
Year of Testing
U-Beams:
550 to 940 in.2
[ data from UTPCSDB Filtered Database, N = 1138 ]
60%
1%

## Slide 65: Conclusions & Advice
Research is a fluid, cyclic process; the original question asked may become unimportant by the end
Don’t be afraid to think outside the box – just because something “should be” doesn’t mean it “is”
Equations learned in class were developed somewhere, verified somehow; it’s nice to know where and how
Getting involved, hands-on, is the best way to understand how something works

## Slide 66: Questions or Comments?

## Slide 67: SHEAR STRENGTH: Horizontal Shear in Prestressed Beams

## Slide 68: Horizontal Shear in Prestressed Beams
P
Find horizontal stress on interface and use it to calculate demand
Calculate capacity following shear-friction theory, giving credit to cohesion between concrete sections and clamping force from reinforcement
To verify method, compared demand to capacity at a single point for laboratory tests

## Slide 69: Calculation Method
Horizontal Shear Demand:
average horizontal shear stress
distance from centerline of bearing pad to the ultimate evaluation point
UEP
45°

## Slide 70: Calculation Method
Definition of average horizontal shear stress:
Complementary property of shear
Non-linear analyses showed that average stress was a reasonable approximation of the stress at the critical interface

## Slide 71: Calculation Method
Horizontal Shear Capacity:
steel friction / clamping term
concrete cohesion term
prestress transfer penalty
beam shape / reinforcement detailing factor

## Slide 72: Calculation Method
Horizontal Shear Capacity:
AASHTO shear friction equation

## Slide 73: Calculation Method
Horizontal Shear Capacity:
prestress transfer penalty
Bars near beam end are stressed at prestress transfer, to resist a force equal to 4% of

## Slide 74: Calculation Method
Horizontal Shear Capacity:
beam shape / reinforcement detailing factor

## Slide 75: Horizontal Shear Evaluation Database
Subset of UTPCSDB Evaluation-Level I Database
Specimens removed if:
  post-tensioned
  rectangular or T-shaped
  non-standard beam section
  skewed beam
  insufficient reinforcement information available
HSED contains 69 data points (including 8 U-Beams)

## Slide 76: Horizontal Shear Evaluation Database
Texas 4B28
AASHTO Type I
AASHTO Type II
Texas Type C
AASHTO Type II with deck
AASHTO Type III with deck
Minnesota Type 54
Texas Tx70 with deck
PCI BT-63 with deck
Texas Tx46 with deck
PCEF-45
Texas Tx28 with deck
Minnesota Type 54 with deck
Texas 5B40
Texas 5XB40 with deck
Texas U54 with deck
Texas Modified U54 with deck

## Slide 77: Horizontal Shear Evaluation
1.0
exceed calculated shear capacity
1.0
horizontal shear damage expected
[calculated using AASHTO General Procedure]

## Slide 78: Horizontal Shear Evaluation
1.0
exceed calculated shear capacity
1.0
horizontal shear damage expected
U-Beams
[ Phase I ]
most beam tests
U-Beams
[ Phase II ]
[calculated using AASHTO General Procedure]

## Slide 79: Horizontal Shear Evaluation
NO horizontal shear damage
[calculated using AASHTO General Procedure]

## Slide 80: Horizontal Shear Evaluation
SOME horizontal shear damage
[calculated using AASHTO General Procedure]

## Slide 81: Horizontal Shear Evaluation
Some Horizontal Shear Damage
No Horizontal Shear Damage
[calculated using AASHTO General Procedure]

## Slide 82: Horizontal Shear in U-Beams
Some Horizontal Shear Damage
No Horizontal Shear Damage
[calculated using AASHTO General Procedure]

## Slide 83: Horizontal Shear in U-Beams
including
without
Some Horizontal Shear Damage
No Horizontal Shear Damage
[calculated using AASHTO General Procedure]

## Slide 84: Horizontal Shear in U-Beams
What is and where did it come from?

## Slide 85: HSED without U-Beams
Some Horizontal Shear Damage
No Horizontal Shear Damage
[calculated using AASHTO General Procedure]

## Slide 86: HSED with U-Beams
Some Horizontal Shear Damage
No Horizontal Shear Damage
[calculated using AASHTO General Procedure]

## Slide 87: Horizontal Shear in U-Beams
#1
#1
#2
#2

## Slide 88: Horizontal Shear in U-Beams
#1
#1
#2

## Slide 89: Shear Friction
Reinforcement

## Slide 90: Shear Friction
Side view of theoretical shear friction specimen with distributed reinforcement
Side view of theoretical shear friction specimen with asymmetrical reinforcement

## Slide 91: Horizontal Shear in U-Beams
P
P
critical plane

## Slide 92: Horizontal Shear in U-Beams
WEB
Bottom Flange
12 in.
5 in.
Critical Interface

## Slide 93: Horizontal Shear in U-Beams
WEB
Bottom Flange

## Slide 94: Horizontal Shear in U-Beams
P
P
2.25in.
CENTERED BAR SPECIMEN
1in.
OFFSET BAR SPECIMEN

## Slide 95: Horizontal Shear in U-Beams
critical interface
bottom flange
web

## Slide 96: Horizontal Shear in U-Beams
bottom flange
web
CENTERED BAR
OFFSET BAR

## Slide 97: Horizontal Shear in U-Beams

## Slide 98: Modified Push-Off Results
Calculated capacity = 74.4 kip
 |  | Centered | Offset
Series 1 | Measured Value | 67.4 kip | 54.7 kip
Series 2 | Measured Value | 73.2 kip | 60.1 kip

## Slide 99: Modified Push-Off Results
Calculated capacity = 74.4 kip
 |  | Centered | Offset
Series 1 | Measured Value | 67.4 kip | 54.7 kip
 | Ratio to Calculated | 0.91 | 0.73
Series 2 | Measured Value | 73.2 kip | 60.1 kip
 | Ratio to Calculated | 0.98 | 0.81

## Slide 100: Modified Push-Off Results
 |  | Centered | Offset | Ratio: | Offset | 
 |  |  |  |  | Centered | 
Series 1 | Measured Value | 67.4 kip | 54.7 kip | 0.81 |  | 
 | Ratio to Calculated | 0.91 | 0.73 |  |  | 
Series 2 | Measured Value | 73.2 kip | 60.1 kip | 0.82 |  | 
 | Ratio to Calculated | 0.98 | 0.81 |  |  | 
for U-Beams with offset reinforcement (i.e., no supplementary bars), reduce capacity with equal to 0.8

## Slide 101: Horizontal Shear Evaluation
Some Horizontal Shear Damage
No Horizontal Shear Damage
[calculated using AASHTO General Procedure]